SECTION 14423

CURVE INCLINE WHEELCHAIR LIFT: OMEGA

Display hidden notes to specifier. (Don't know how? Click Here)

** NOTE TO SPECIFIER **  Savaria Inc.; Incline Wheelchair Lifts.
 .
This section is based on the products of Savaria Inc, which is located at:

Savaria Inc.: 107 Alfred Kuehne Blvd, Brampton, Ontario, L6T 4K3 Toll Free: 800-661-5112. Tel: (905) 791-5555. Fax: (905) 791-2222 Email: info@savaria.com Web www.savaria.com

Savaria is an international company specializing in the manufacturing of accessibility products.  A world leader in the accessibility industry with a reputation for quality and reliability, Savaria has over 50,000 various products installations worldwide and many innovative products.
 
The Omega inclined platform wheelchair lift is able to travel along straight or curving stairways, up several flights of stairs and across horizontal landings.  The Omega's simple control system allows for dependability and reliability. The Omega can travel on the inside or outside radius of the stairway, offering the optimum in design flexibility.

- GENERAL

  - SECTION INCLUDES

** NOTE TO SPECIFIER **  Delete items below not required for project.

    - Indoor inclined platform wheelchair lifts.

    - Outdoor inclined platform wheelchair lifts.

    - Portable emergency evacuation device.

  - RELATED SECTIONS

** NOTE TO SPECIFIER **  Delete any sections below not relevant to this project; add others as required.

    - Section 03300 - Cast-In-Place Concrete:  Anchor placement in concrete.

    - Section 04800 - Masonry Assemblies:  Anchor placement in masonry.

    - Section 06100 - Rough Carpentry:  Blocking in framed construction for lift attachment.

    - Section 09260 - Gypsum Board Assemblies:  Stair walls.

    - Section 13650 - Fire Alarm System: Building Fire Alarm Integration system to connect the lift control system with the building fire alarm system.

    - Division 16 - Electrical:  Electrical power service and wiring connections.

    - Division 16 - Electrical:  Concealed low voltage control wiring.

    - Division 16 - Electrical:  Intercom and wiring.

  - REFERENCES

** NOTE TO SPECIFIER **  Delete references from the list below that are not actually required by the text of the edited section. Use ASME references for installations in the United States. Use CSA references for installations in Canada. Add International references as required.

    - ASME A17.5 - Elevator and Escalator Electrical Equipment.

    - ASME A18.1a 2001 - Safety Standard for Platform Lifts and Stairway Chairlifts.

    - ASME A18.1, Section 6, Private Residence Inclined Platforms.

    - CSA B44.1 - Elevator and Escalator Electrical Equipment.

    - CSA B355 - Lifts for Persons with Physical Disabilities.

    - CSA B613-00 Private Residence Lifts for Persons with Physical Disabilities.

    - ICC/ANSI A117.1 - Accessible and Usable Buildings and Facilities.

    - NFPA 70 - National Electric Code.

    - CSA - National Electric Code.

  - SUBMITTALS

    - Submit under provisions of Section 01300.

    - Product Data:  Manufacturer's data sheets on each product to be used, including:

      - Submit manufacturer's installation instructions, including preparation, storage and handling requirements.

      - Include complete description of performance and operating characteristics.

      - Show maximum and average power demands.

    - Shop Drawings:

      - Show typical details of assembly, erection and anchorage.

      - Include wiring diagrams for power, control, and signal systems.

      - Show complete layout and location of equipment, including required clearances.

** NOTE TO SPECIFIER **  Delete selection samples if colors have already been selected.

    - Selection Samples:  For each finished product specified, two complete sets of color chips representing manufacturer's full range of available colors and patterns.

    - Verification Samples:  For each finished product specified, two samples, representing actual product, color, and patterns.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications:	Firm with minimum 5 years documented experience in manufacturing of inclined wheelchair platform lifts.

    - Installer Qualifications:  Firm licensed to install equipment of this scope, with evidence of experience with specified equipment.  Installer shall maintain an adequate stock of replacement parts and have qualified people available to ensure timely maintenance and callback service at the project site.

  - REGULATORY REQUIREMENTS

** NOTE TO SPECIFIER **  Edit and delete one of the two following paragraphs to suit local requirements.  First paragraph is for installations in the United States. Second paragraph is for installations in Canada.

    - Provide platform lifts in compliance with:

      - ASME A18.1 - Safety Standard for Platform Lifts and Stairway Chairlifts.

      - ASME A17.5 - Elevator and Escalator Electrical Equipment.

      - NFPA 70 - National Electric Code.

    - Provide platform lifts in compliance with:

      - CSA B355 - Lifts for Persons with Physical Disabilities.

      - CSA B44.1/ASME A17.5 - Elevator and Escalator Electrical Equipment.

      - CSA - National Electric Code.

** NOTE TO SPECIFIER **  Include and edit the following paragraph as required for seismic requirements. Delete if not required.

    - Seismic Design: In accordance with seismic risk zone rating in accordance with local code, if required.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer's unopened packaging until ready for installation.

    - Store components off the ground in a dry covered area, protected from adverse weather conditions.

  - PROJECT CONDITIONS

    - Do not use wheelchair lift for hoisting materials or personnel during construction period.

  - WARRANTY

** NOTE TO SPECIFIER ** The manufacturer’s basic warranty is a limited 3 year warranty for the replacement at no cost of defective parts but does not include the labor costs required to replace the defective parts. Warranty requires maintenance agreement during period of the warranty. Delete if not required.

    - Warranty: Provide a three (3) year limited warranty covering replacement of defective parts and excluding labor. Preventive maintenance agreement required.

  - MAINTENANCE SERVICE

    - Furnish service and maintenance for elevator system and components for the following period from Date of Substantial Completion.

      - One year.

      - Two years.

      - Three years.

      - Four years.

      - Five years.

    - Include systematic examination, adjustment, and lubrication of elevator equipment. Repair or replace parts whenever required. Use parts produced by manufacturer of original equipment. Replace wire ropes when necessary to maintain required factor of safety.

    - Provide emergency call back service for this maintenance period.

    - Perform maintenance work using competent and qualified personnel approved by elevator manufacturer or original installer.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:  Savaria Concord Lifts Inc.: 107 Alfred Kuehne Blvd, Brampton, Ontario, L6T 4K3 Toll Free: 800-661-5112. Tel: (905) 791-5555. Fax: (905) 791-2222 Email: info@savaria.com Web www.savaria.com

** NOTE TO SPECIFIER **  Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

    - Substitutions:  Not permitted.

    - Requests for substitutions will be considered in accordance with provisions of Section 01600.

  - STAIR LIFT FOR STRAIGHT OR TURNING STAIRWAYS

    - Inclined Platform Lift: Savaria Stair-Lift¸ Model Omega inclined platform lift for straight and turning stairways. Lift consists of a tubular guide rail system¸ a folding platform that is moved along the guide rails by a rope sprocket drive system¸ overspeed safety system and call stations at each landing. Conform to the following design requirements:

      - Application:

** NOTE TO SPECIFIER **  Select one of the following two paragraphs and delete the one not required.

        - Indoor.

        - Outdoor.

      - Platform Load Rating:  550 lb (250 kg) with minimum safety factor of 5.

      - Travel Speed:  14 fpm (0.07 m/s) nominal

      - Platform Deck:  16 gauge (1.6 mm) sheet metal coated with electrostatically applied and baked anti-skid paint.

** NOTE TO SPECIFIER **  Select the following paragraph for standard ADA compliant platform size. Delete if not required.

        - Platform Size A (ADA Compliant):  30.50 in (775 mm) wide by 49.20 in (1250 mm) long.

        - Platform Size B:  28.30 in (720 mm) wide by 35.40 in (900 mm) long.

      - Platform Operation:

        - Automatic Fold:  Folded and unfolded electrically from the call station.

        - Emergency Manual Fold:  When unit is left in the open position¸ platform may be manually folded and retained in closed position.

      - Under Platform Obstruction Sensing:

        - Provide an under platform sensing device to stop the platform from traveling in the downward direction when encountering 4 lb (1.8 kg) of pressure.

        - Platform is permitted to travel in the opposite direction of obstruction to allow clearing.

      - Passenger Restraining Arms:

        - Platform equipped with retractable passenger restraining arms in compliance with ASME A18.1a.

        - Arms stop moving when an obstruction is encountered and will immediately retract when the signal is removed.

        - Provide with means to manually unlock and open the restraining arms for passenger emergency evacuation.

        - Arms are folded and unfolded electrically from the call stations or platform controls.

        - Arms mounted 39 in (990 mm) above the platform deck. When in guarding position the arms are located above the perimeter of the platform.

        - The gaps between ends of arms shall not exceed 4 in (100 mm).

      - Boarding Ramps:

        - Provide boarding sides of platform with retractable ramps positioned for travel at a height of 6 in (152 mm) measured vertically above the platform deck.

        - Lock ramps in their guarding positions during travel. When the platform is at the landing, only the retractable ramp servicing the landing shall be operable.

        - Ramps shall be folded and unfolded electrically.

        - Retractable ramps¸ in the guarded position¸ shall withstand a force of 125 lb (556 N) applied on any 4 in (100 mm) by 4 in (100 mm) area. This force shall not cause the height of the ramp¸ at any point in its length¸ to be less than 6 in (152 mm) measured vertically above the platform deck.

        - Provide a means to manually unlock the ramps for emergency evacuation when platform is located at a landing.

        - Provide with a directional obstruction sensitive device on the travel direction side end of the platform to stop lift when an obstacle of 15 lbf (70 N) is encountered. Platform is permitted to travel in the opposite direction of obstruction to allow clearing.

        - When platform folds¸ passenger restraining arms shall fold down and be covered by the folded platform.

      - Platform Side Wall:

        - Provide non-boarding and non-guide-rail side of the platform with a sidewall of not less than 6 in (152 mm) in height¸ measured vertically from the platform deck.

      - Hand Grips:

        - Equip platform with one handgrip centered on the platform at 36.50 in (925mm) and 12 in (305mm) long

      - Clearance Dimensions:

        - When folded platform shall not protrude more than 17.50 in (445 mm) from mounting surface.

        - When unfolded and in use platform shall not protrude more than 41.50 in (1050 mm) from wall.

      - Controls:

        - Platform Controls: 24 V Low Voltage type.

        - Platform equipped with emergency stop switch located within reach of the passenger 43 in (1090 mm) above platform deck. When activated emergency stop button shall cause electric power to be removed from the drive system stopping lift immediately.

        - Operating controls shall be two separate constant pressure buttons with directional arrows on a removable hand pendant device with emergency stop button.

        - When platform arrives at landing the user keeps pressing the directional button and the passenger restraining arms and boarding ramp shall unfold automatically allowing passenger to disembark.

        - Platform shall be equipped for:

** NOTE TO SPECIFIER ** Select key switch or keyless operation. Delete paragraph not required for the Project.

          - Keyed operation.

          - Keyless operation.

      - Passenger Seat:  Fold-down type with safety belt. Minimum rated load of 250 lb (115 kg).

** NOTE TO SPECIFIER ** The following paragraphs are optional platform lift features.  Delete paragraphs for features not required for the Project.

      - Side Loading Platform: Provide with automatic folding ramps and kickplates at boarding sides of platform.

      - Platform Security Lock: Provide mechanical locking system to prevent unauthorized unfolding of the platform.

      - Attendant Hand Held Pendant Control: Provide with plug-in socket on platform control panel.

      - Pedestrian Audio Alert:  Provide chime mounted on platform to indicate platform is folded up and in motion, traveling on stairway.

** NOTE TO SPECIFIER ** Select the following paragraph when alarm is required to meet local code requirements or for remotely located lifts.

      - Platform On Board Emergency Alarm:  Provide platform with on board alarm that sounds when emergency stop button is pushed.

      - Remote Platform Boarding:  Platform shall travel beyond standard boarding position to remote boarding location away from stairs. Provide with ramp extensions 3 inch (76 mm) extruded aluminum added to the boarding ramps.

** NOTE TO SPECIFIER ** Select the following paragraph where required. Delete if not required.

      - Under Carriage Sensing: Provide bottom of platform hanger with a sensing plate to stop the platform from traveling in the downward direction when encountered with 4 lb (1.8Kg) of pressure. It shall be possible to drive the platform away from the obstruction.

      - Side of Carriage Obstruction Device: Provide a sensor that detects obstructions in the path of the side of the hanger. Lift shall stop immediately and not travel until the obstruction is removed. It shall be possible to drive the platform away from the obstruction.

    - Drive and Guide Rail System

      - Operation:

        - Motor: 1.0 hp (0.75kW) electric motor with an integrated brake (Up to 3.0 hp (2.2 kW) over 100 ft (30m) of travel).

        - Required power: 208-240 VAC¸ single phase¸ 60 hz. on a dedicated 20 amp circuit.  Rated current shall be up to 9 amps (for 2.2kW motor) for operation with rated load.

        - Locate roped sprocket drive system consisting of a motor¸ gearbox and controller (AC Drive) at the upper end of the tubes.

        - Equip drive with an emergency manual lowering system with kill switch when emergency manual lowering system is engaged.

** NOTE TO SPECIFIER ** Select one of the following two drive cabinet paragraphs. The first paragraph is optional and the second paragraph is a space saving alternative which is standard.  Delete paragraph not required for the Project.

      - Full enclosed Drive Cabinet:

        - Cabinet: 22 in (560 mm) wide by 55 in (1400 mm) high by 11.50 in (290 mm) deep located at top landing.

        - Cabinet door is key locked and monitored with an electrical cutout safety switch.

        - Provide an integrated lockable main disconnect switch and breaker remotely located and separate from the drive cabinet.

      - Compact Drive Cabinet with Separate Control Box:

        - Compact drive cabinet will house all mechanical drive system components and shall be located at the end of the tube system at top landing.

        - Controller box will contain all the electrical components of the drive system and be located up to 50 feet (15 m) linear away from the compact drive. Control box dimensions are 20 in (510 mm) wide by 20 in (510 mm) high by 11.50 in (290 mm) deep.

        - Provide an integrated lockable main disconnect and breaker in the compact drive control box.

      - Guide Rail:

        - Construct of two 2 in (51 mm) diameter steel tubes spaced 22 in (560 mm) apart vertically at right angle from rail. Tubes will run parallel to the stairs and horizontal to landings throughout the length of travel.

        - When negotiating a horizontal landing a third 2 in (51 mm) diameter steel tube shall be added to the tube system to guide and stabilize platform.

        - Tube system shall not protrude more than 7.50 in (190 mm) from the wall with support posts.

        - Suspension means contained in the tubes shall be a 3/8 in (9 mm) diameter galvanized steel core wire rope with a minimum breaking strength of 12 540 lb (5700 kg).

        - Locate overspeed safety at the bottom of the tube assembly and shall consist of a mechanical overspeed sensor and brake with electrical drive cut-out protection.

        - Provide a final limit switch at the upper and lower end of the tubes to stop the platform if it travels past the normal terminal stopping device.

** NOTE TO SPECIFIER ** The following paragraph is optional. Delete if not required for the Project.

      - Auxiliary Power (Optional): Provide battery back-up system (UPS) for normal up / down lift operation during power failure for a minimum of five (5) trips with rated load.

** NOTE TO SPECIFIER ** Select the following paragraph where required to keep stairway clear when lift is not in use. Delete if not required.

      - Platform Storage Beyond Upper/Lower Landings:

        - Platform shall travel in the folded position beyond the upper landing at the top stair nose to a remote parking position away from the stairs.

        - Platform shall travel in the folded position beyond the lower landing to a remote parking position. Provide with a ramp extension for this configuration.

** NOTE TO SPECIFIER ** The following paragraph is required for certain stair configurations. Delete if not required for the Project.

      - Final Limit Switch at Lower Landing:  Platform will land over a flight of stairs and will have a final lower limit switch.

** NOTE TO SPECIFIER ** Select one of the following rail mounting paragraphs and delete the ones not required. Direct mounting is recommended only for solid concrete walls. Use of steel support posts is for installations where there is no wall to attach to or where wall construction does not provide enough strength. Consult the Savaria Omega Planning Guide for further rail mounting information and a loading diagram.

      - Rail Mounting:

        - Direct Mount Solid Walls: Rails directly mounted to the stairway wall.

        - Tower Mount Struts: Provide with 2.50 in (65 mm) by 2.50 in (65 mm) hollow structural steel tubular posts to support the guide rails.

      - In-Fill Safety Panels: Provide a filler panel system to act as a barrier where existing handrails are removed and there is no wall behind the lift. Filler panels between the support posts shall cover any open area behind the rail to protect against shear hazards.

** NOTE TO SPECIFIER **  Select one of the following two paragraphs for in-fill safety panels.  Delete the paragraphs not required for the Project.

NOTE to SPECIFIER:  If using paragraph below add information on material to be used as a filler panel such as glass or Plexiglas.

        - Filler Panel Mounting Brackets: Brackets welded to support posts to allow for a barrier panel system supplied by others.

          - Filler Panel provided by others: ____________________.

** NOTE TO SPECIFIER ** The following paragraphs may be required to meet local code requirements. This is an alternate to infill panels. Delete if not required for the Project.

        - Steel Tube Filler: Provide additional 2 in (51mm) diameter steel tubes added to the guide rail system for aesthetics or to create a further safety barrier with a maximum 6 inch (152 mm) opening between tubes (when possible).

** NOTE TO SPECIFIER ** With the installation of guide rails existing handrails are often obstructed or removed. The following paragraphs represent the minimum requirements for adding optional pedestrian handrails. Edit as required for the Project.

    - Pedestrian Handrail Integrated with Guide Rail:

      - A third rail acting as a handrail shall be added where existing handrails are either removed or blocked by the lifting equipment (when possible).

      - The handrail gripping surface shall have a smooth gripping surface 1.50 in (38 mm) in diameter.

      - Handrail shall be in the same vertical plane as the guide rail system.

      - Handrails shall be mounted to the tube assembly.

    - Call Stations:

      - Provide a call station at each serviced landing.

      - Call stations¸ 24 V low voltage with four control buttons: one touch platform fold¸ one touch platform unfold and two directional call and send buttons.

** NOTE TO SPECIFIER ** The following paragraphs include additional or optional call station features. Select and edit paragraphs required and delete those not required for the Project.

      - Provide intermediate stops between the upper and lower landings at the following locations:

        - As indicated on the Drawings.

        - _________________.

        - _________________.

      - Call stations shall be equipped for:

** NOTE TO SPECIFIER ** Select key switch or keyless operation. Delete paragraph not required for the Project.

        - Keyed operation.

        - Keyless operation.

** NOTE TO SPECIFIER ** The following paragraph is optional delete if not required for the Project.

      - Provide Attendant Call buttons on each call station when required.

** NOTE TO SPECIFIER ** Select the call station mounting requirements from the following paragraphs and delete the ones not required. Surface mounting call stations are included with the lift as standard equipment (subject to change).

      - Call Station Mounting:

        - Lower and Intermediate landing call station.

          - Provide surface mounted call station.

          - Provide flush mounting call station painted finish collars to trim all call stations that are recessed into the walls.

        - Upper landing call station.

          - Provide surface mounted call station on guide rail drive box (optional).

          - Surface mount on wall.

          - Provide flush mounting call station painted finish collars to trim all call stations that are recessed into the walls.

        - Provide free-standing mounting pedestals for call stations located as follows:

          - Lower landing.

          - Intermediate Landing.

          - Upper landing.

** NOTE TO SPECIFIER **  Select additional safety or code requirements from the following paragraphs and delete those not required.

    - Additional Safety or Code Requirements

      - Wall Mounted Audio Visual Alerts:  Provide with adjustable volume control that sound while the lift is in operation and are visible by pedestrian traffic from all flights and landings.

      - Building Fire Alarm Integration (Optional):  Coordinate with Section 13650 Building Fire Alarm System to connect the lift control system with the building fire alarm system. If the lift is not in operation when the building fire alarm system is activated power will be cut to the lift preventing use during fire evacuation.  If the lift is in use when the building fire alarm system is activated, the lift shall only allow the passenger to travel to the designated landing with the emergency exit.

** NOTE TO SPECIFIER **  The following paragraphs include provisions for indoor and outdoor locations. Select the paragraph required and delete those not required.

    - Finish Environment Requirements:

      - Design and fabricate lift to manufacturer's standard design for indoor location.

** NOTE TO SPECIFIER **  Select the following paragraph for aesthetic or outdoor use. Delete if not required.

      - Stainless Steel Components (optional):  Design and fabricate lift using the following:

        - Guide rails shall be supplied in stainless steel.

        - Handrails shall be supplied in stainless steel.

        - Support towers shall be supplied in stainless steel.

        - Drive box shall be supplied in stainless steel.

        - Wall mounted audio visuals shall be supplied in stainless steel.

        - Platform sensing plate shall be supplied in stainless steel.

        - Fasteners for rail assembly and anchoring shall be supplied in stainless steel.

** NOTE TO SPECIFIER **  Select the following paragraph for outdoor use. Delete if not required.

      - Design and fabricate lift to manufacturer's standard design for outdoor location.

        - Lift to include all modifications recommended by manufacturer for reliable performance in outdoor climate of lift installation site.

        - Provide an outdoor weatherproofing package including zinc rich primer on steel surfaces, weather-resistant sealant on the electrical components, stainless steel or plated fasteners and a weatherproofed stainless steel or zinc plated drive box.

        - Platform control cover shall be fabricated of a Silver Grey injection-molded polymer.

      - Painting: After pretreating paint with electrostatically applied and baked powder coat as follows:

** NOTE TO SPECIFIER ** Select the paragraph for standard or custom color and delete the one not required.

        - Fine Textured Light Grey (RAL 7035).

        - Custom color as selected by Architect from manufacturers standard RAL colors.

END OF SECTION

Revision 001, jan 2012